## Comment Template
Template for comments / observations returned during the consultation |  | Date: | Document: Public consulttion on draft " Fire Safety Guide for Building owners and Operators"
Name of Organisation / Respondent | Heading / Section No. / Appendix No. / Table No. or Diagram No. (e.g. Interpretation / Section 2.1.2.6 / Appendix B.5.1.1) | Type of comment G = General E = Editorial T = Technical | Comment / Observation | Proposed change (if any)
Engineers Ireland | General document | G | Poor definitions of role requirements | Clearly define requirements for each of the roles outlined in the legislation to demonstrate competence. Provide examples of qualified and competent persons.
Engineers Ireland | General document | E | Throughout the document there are a number of typographic errors that gives the impression that automatic spelling changing had been turned off in the original document. Examples Page 7 4.1 “thissection” “ensuringthe” Page 26 6.2 “dutyon” Page 33 6.5 “icomplex/naccessible” | Turn on the automatic spelling checking and proofread the document for errors
Engineers Ireland | General document | G | This document has a number of references to British Standards and documents from UK organisations which now post BREXIT may cause potential future issues with maintaining continuing compliance with European Standards. Examples Page 51 “BS 8458 Water mist systems” Page 53 “BS 7346-8:2013 Smoke control systems” Page 54 “BS 9990 Fire hydrants/Mains” Page 55 BS 9991 “Standby Generators” Page 56 “BS 8214 Fire Doors” Page 76 D.3 “BS 7346-8:2013” Page 77 “Fire Door Alliance/BWF” note changed web site https://firedoors.bwf.org.uk. Also pages 78, 79 contains a BWF checklist. | Suggest taking out the reference to the British Standard and copy the relevant text in accordance with international copyright/intellectual property law
Engineers Ireland | Section 3.0 | E | In addition to end of the second paragraph on page 5 defining how to ensure processes are clear to all parties'…should be clear between all parties involved' | Add "through regular checks and training."
Engineers Ireland | Page 15 Section 5.2.1 Emergency Procedures | T | Consideration should be given to responding to alarms outside normal working hours (for example Public Holidays). There may be a requirement for alternative coverage by a caretaker or management company during these times. In business, such calls could be rerouted to a call centre or alternative contact. | Discuss with industry representative what alternative solutions are currently used.
Engineers Ireland | Section 5.2.3 | T | Information missing about other combustable gases such as compressed oxygen etc. Compressed gases can be extremely dangerous in a fire. | ISO 11625:2007 - Gas cylinders — Safe handling or similar
Engineers Ireland | Section 5.3.3 | T | Fire Safety instructions for ocuupants focuses on people in buildings organised by others, it doesn’t highlight specifically hybrid workers and training and processes needed for them. | Highlight considerations for hybrid working and highlight good practice in housekeeping and training.
Engineers Ireland | Page 17 Section 5.4 Checking of Escape Routes | T | During times of property refurbishment or modification some existing escape routes may be impacted. The group responsible for such work should assess and document such risks and any proposed changes to existing escape routes. Allowance should be made for modification to signs and emergency lighting for the duration of the works. | Discuss with industry representative best practice for handling of property works for the safe provision of escape routes.
Engineers Ireland | Page 18 Section 5.5.2 Assisting the Fire Brigade | T | Industrial sites commonly have a design feature for barrier systems controlling access to private roads, that the barriers will automatically open in emergency conditions to reduce Fire Tenders delay in entering the site and allow emergency evacuation of people. | Discuss with industry representative best practice for barrier systems for these types of properties
Engineers Ireland | Section 6.2 | T | The sounders depicted in figure 4 are not loop powered sounders, the operation of a manual call point or point detector would impose an excesive alarm load which could cause the detection loop to cease operation in the event of a fire. | Change image in the circuit to a loop powered sounder or show a separate circuit for the sounders.
| Section 6.2 | T | Figure 6 in the document reads ‘Illustrative Fire Alarm and Detection System in a Building’ should read ‘Fire Detection and Alarm System’ as in FDAS. Figure 6 does not reflect I.S.3218:2013+A1:2019 clause 6.6.4.1 recommendations for sounders in bedrooms from the landlord system to ensure 75dB(A) at the bedhead from the landlord FDAS. For the Quarterly and Yearly maintenance the word ‘should’ should be replaced with the word ‘shall’ as per I.S.3218:2013+A1:2019
Engineers Ireland | Section 6.3 | E | Disabled refuge & externally illuminated escape route safety signs omitted. | Insert both areas
| Section 6.3 | T | It appears only the more common points of emphasis were included as detailed in Figure 8 in the document. Other Points of emphasis should also include (Electrical) switch rooms as per I.S.3217:2013+A1:2017 clause 8.5.2.5 and Annex D Table D.1 and lift cars as per clause 8.5.2.1 and Annex D Table D.1.
Engineers Ireland | Section 6.3 | T | Inclusion of the requirement that each emergency lighting system to have a test facility | Insert ''each emergency lighting system shall have a suitable facility for simulating failure of the normal supply for test purposes''.
Engineers Ireland | Section 6.3 | G | No entry for system modifications in the sample emergency lighting logbook | Insert a column in the log book to record any system modifications or changes to the layout of the building since the last service visit.
| Section 6.4 | T | Maintaining door/frame/floor gap tolerances is a key aspect of the performance of a fire door. | Gap tolerances are detailed in Figure 14 and should be mentioned in the commentary below Figure 14 in the paragraph pertaining to regular checks. (listed in Table 2 of document)
| Section 6.5 | T | The paragraph above Figure 16(a) should also include the operation of Automatic Air Release Valves at high points to ensure efficient charging of riser. (not listed in table 2)
Engineers Ireland | Section 5.2.4 | G | An interval between the testing & inspection of electrical installations and appliances should be recommended. | Declare a period for testing & the inspection of electrical installations & appliances i.e., quarterly or annually.
Engineers Ireland | Annexe E2 | G | No entry for system modifications in the sample fire alarm logbook | Insert a column in the log book to record any system modifications or changes to the layout of the building since the last service visit. Any changes may affect the catergory of fire detection afforded by the original designer.
Engineers Ireland | Appendix | T | Guidance on fire risk assessment omitted | Create an additional appendix item showing guidance and considerations to create a fire safety risk assessment. Identifying risk and severity.
Engineers Ireland | Page 49-60 Section 8.0 Recommended Routine Maintenance Schedules and following table 2 | T | A significant proportion of the population are colour blind so propose using a code instead of colour for categorisation in the tables. | Replace colour coding with an alternative code suitable for people with colour blindness
Engineers Ireland | Pages 61-63 Web links | T | Since this document was originally drafted the structure of the gov.ie web site has changed. | Check and revise the links on this page